## Slide 1
TRIDENT

## Slide 2: DISTRICTS OF İNEGÖL
Boğazköy
Çavuşköy
Halhalca
Karagölet
Sungurpaşa
Şehitler

## Slide 3: DESIGN PROCESS
Population Projection Analysis
Water Demand Estimation
Water Tanks
Routes
Quantity Take-Off

## Slide 4
Population Projection Analysis
Merve YAVUZ

## Slide 5
Population Projection Analysis

## Slide 6
 | Census Data |  |  |  |  | 
Years | Boğazköy | Çavuşköy | Halhalca | Karagölet | Sungurpaşa | Şehitler
1980 | 678 | 565 | 573 | 353 | 800 | 784
1985 | 711 | 592 | 510 | 377 | 746 | 811
1990 | 690 | 596 | 529 | 337 | 747 | 820
2000 | 602 | 623 | 406 | 263 | 647 | 753
2007 | 464 | 541 | 333 | 190 | 575 | 641
2008 | 541 | 528 | 331 | 184 | 569 | 638
2009 | 483 | 501 | 309 | 183 | 475 | 639
2010 | 505 | 490 | 294 | 167 | 442 | 628
2011 | 499 | 476 | 285 | 173 | 430 | 619
2012 | 517 | 453 | 279 | 167 | 404 | 610
2013 | 494 | 444 | 285 | 163 | 398 | 610
2014 | 490 | 428 | 280 | 170 | 388 | 592
Table 1: Census data for all districts

## Slide 7
Gathering the past records of census results,
Investigating the socio-economic developments.

## Slide 8
The Arithmetic Extrapolation Method
The Geometric Extrapolation Method
The Turkish Bank of Provinces Method
Logistic S-curve method
Declining growth rate method
Population Projection Analysis Methods

## Slide 9
According to the Turkish Bank of Provinces Specification, at least 3 methods should be used.
The Arithmetic Extrapolation Method,
The Geometric Extrapolation Method,
The Turkish Bank of Provinces Method.

## Slide 10
Chart: The projected years vs The projected populations
| 2014 | 2015 | 2020 | 2025 | 2030 | 2035 | 2040 | 2045 | 2050
Bank of Prov. (ç) | 428 | 432 | 454 | 478 | 502 | 527 | 554 | 583 | 612
Art. Exp. (Ka) | 428 | 432 | 454 | 475 | 496 | 518 | 539 | 561 | 582
Geo. Exp. (Kg) | 428 | 440 | 503 | 574 | 657 | 751 | 858 | 981 | 1121
Figure 1: The Projected Population values of Çavuşköy between 2014-2050

## Slide 11
 |  | The Projected Population values by Turkish Bank of Provinces Method |  |  |  |  | 
The Projected Years | Çchs | Boğazköy | Çavuşköy | Halhalca | Karagölet | Sungurpaşa | Şehitler
2014 | 1 | 490 | 428 | 280 | 170 | 388 | 592
2015 | 1 | 495 | 432 | 283 | 172 | 392 | 598
2020 | 1 | 520 | 454 | 297 | 180 | 412 | 628
2025 | 1 | 547 | 478 | 312 | 190 | 433 | 660
2030 | 1 | 575 | 502 | 328 | 199 | 455 | 694
2035 | 1 | 604 | 527 | 345 | 210 | 478 | 730
2040 | 1 | 635 | 554 | 363 | 220 | 503 | 767
2045 | 1 | 667 | 583 | 381 | 231 | 528 | 806
2050 | 1 | 701 | 612 | 401 | 243 | 555 | 847
Table 2: The Projected Population values by Turkish Bank of Provinces Method

## Slide 12: Estimation of Water Demand Quantity
Mustafa YILMAZ

## Slide 13
Factors that Effect Water Demand
Population values
Socio – Economic development
Water quality
Climate
Unit price of water

## Slide 14
Water Demand Quantity based on Population values
Table 3: The water demand quantity of Çavuşköy

## Slide 15
Animal Species | Quantity (l/day)
Bovine | 50
Ovine | 15
Chicken-Duck | 0,25
Water Requirement of Livestock
According to the General Directorate of State Hydraulic Works;
Table 4: The water requirement of livestock

## Slide 16
Water Requirement of Other
Regional Boarding School: 100 liter/p/day
School that gives mobile education: 50 liter/p/day
Military Buildings: 100 liter/p/day
Factory and big offices: 50 liter/p/day
Hotel, Motel, Summer houses: 200 liter/p/day

## Slide 17
Selection of Peak Coefficient
Table 5: The water demand quantity of Çavuşköy

## Slide 18
The Maximum Daily Water Demand of each District
Table 6: The maximum daily water demand of each district

## Slide 19: Water Tanks
Gökberk SIĞINIR

## Slide 20: Water Tank Placement Criteria
Being near to District
  Direction of the Water Resources
  Topography & Master Plan
Hydrology
Economic conditions

## Slide 21: Water Tank Types
Prismatic Tank
Tower Tank

## Slide 22: Elevation of the Water Tanks
Minimum dynamic pressure
  Highest point +20 m
Maximum maximum static pressure
  Lowest point + 60-65 m
Difference > 45 m
  Upper & Lower Pressure Zones

## Slide 23: Calculation Example : Şehitler
The maximum settled elevation: 518 m
The minimum settled elevation: 440 m
Diffrence =78m > 45m 2 pressure zones
505
485
440
538
518
473
65
20
20
65

## Slide 24
Table 7: The lower and upper pressure zones for each district

## Slide 25: Volume of the Water Tanks
Hourly & Daily Water Consumption
Qwater (in case of Fire)
Emergency Need
Balancing the Efficiency Variance in Water Resources

## Slide 26: Calculation of the Volume of the Water Tanks
Ʃ VWATER TANK = VBalanced + VFire + VEmergency Need
Ʃ VWATER TANK = ( * Daily Consumption ) + (QFire*t) + ( Daily Consumption * 0.1)

## Slide 27: The Calculated Volumes for the Water Tanks
Districts | Volume of daily consumption(m3) | Total volume of water tanks (Vt)
Boğazköy | 137,8 | 95,7
Çavuşköy | 123,0 | 89,3
Halhalca | 68,5 | 65,7
Karagölet | 45,6 | 55,8
Sungurpaşa | 152,0 | 101,9
Şehitler | 145,4 | 99,0
Table 8: The volumes of the water tanks

## Slide 28: Water Supply System Route and Diameter Selection
Ferhat ÜNAL

## Slide 29: Water Supply System Route Selection
Technical and economic aspect
Considered conditions:
  Shortest route
  Easiness of route construction
  Easiness of maintenance and operating

## Slide 30: Route Types
Pumped Discharged Lines
  Pumps
  160m maximum head
  Pump station
Gravity Pipelines
  Gravity and self weight
  80m maximum head
  Trough

## Slide 31: Alternative Route 1

## Slide 32: Alternative Route 2

## Slide 33: Water Supply System Diameter Selection
Pumped Discharge Lines
  Initial investment cost
  Coefficient of friction
  Efficiency of pumps
  Water hammer
  Operating cost
  Bigger diameter Lower head losses and energy
  consumption
  Bigger diameter Higher investment and operating
  cost

## Slide 34: Calculation of Pumped Discharge Lines
De = 1.5 √Qe
Table 9:
Table 10:

## Slide 35: Water Supply System Diameter Selection
Gravity Pipelines
  Velocity
    Minimum 0,3 m/s
    Maximum 3,0 m/s
    Average 1,0 - 1,5 m/s
  Q = V * A
  Trial diameters

## Slide 36: Table 11:

## Slide 37
Table 12:

## Slide 38: Table 13:Quantity Take-Off

## Slide 39: References
İller Bankası – İçme suyu Tesisleri Etüt, Fizibilite Projelerinin Hazırlanmasına ait Teknik Şartname
Devlet Su İşler- Nüfus ve İçme suyu Tahmin Esasları
YANMAZ, M. (16). Applied Water Resources Engineering (pp. 286-287). Ankara, TURKEY: METU Press.
http://orig13.deviantart.net/69ff/f/2013/125/f/1/poseidon_s_trident_tattoo_by_pumpkinsoup-d3fm4v1.png
http://www.google.com.trsearchq=population&espv=2&biw=1366&bih=677&source=lnms&tbm=isch&sa=X&ved=0ahUKEwjY1sjq0qfJAhXJ6CwKHShhCh4Q_AUIBigB&dpr=1#tbm=isch&tbs=rimg%3ACQuUNX-LPIgMIji7tefgePOtXy1hCWCvjOdEn6cybtC5Kz4UqrTBwjq26CiUCB5pruh
http://www.denizlihaber.com/medya/2012/09/b%C3%B6yle+ola...jpg
http://www.uzunkopru.gov.tr/ortak_icerik/uzunkopru/galeri//76/P4287123.JPG
http://www.audiotech.com/trends-magazine/wp-content/themes/Trends

## Slide 40
Thank You